CONDITION BASED ASSESSMENT

QUICK SCANNING REPORT

SBUM DIAGNOSTIC JOHOR

TNB BAHAGIAN PEMBAHAGIAN JOHOR

| FUNCTIONAL LOCATION (ERMS) | : | JJBU/PCE/J03951 |
| --- | --- | --- |
| FUNCTIONAL LOCATION (SITE) | : | JJBU/PCE/J03951 |
| SUBSTATION NAME (ERMS) | : | SK KG MAJU JAYA |
| SUBSTATION NAME (SITE) | : | SEK. KEB. KG. MAJU JAYA |
| COORDINATE | : | 1.579787, 103.718929 |
| SUBSTATION TYPE | : | PCE |
| AREA | : | JOHOR BAHRU |
| STATE | : | JOHOR |
| PO | : | 42234207 |
| DATE | : | 14 JUL 2026 |
| SCANNED BY |  |  |
| THERMOGRAPHY | : | MUHAMMAD OMAR RIDZUAN (2013MY20N010) |
| EQUIPMENT/TOOLS |  |  |
| THERMOGRAPHY | : | FLIR T640 (SN 55912229) (CALIBRATION DUE DATE: 26 DEC 2026) |
| PREPARED BY |  |  |
| NAME OF CONTRACTOR | : | EET ENGINEERING SERVICES SDN BHD |
| ADDRESS | : | NO.38, JALAN SS19/1D, |
|  | : | 47500, SUBANG JAYA, SELANGOR. |
| SUBSTATION SIGNBOARD |  |  |

EXECUTIVE Summary

| NO. | EQUIPMENT | DEFECT AREA | IR (Abs.T) | IR (∆T) | DEFECT |
| --- | --- | --- | --- | --- | --- |
|  | FP TX1 – INCOMING F1 | INCOMING LINK CONNECTION/ RED PHASE | 66.7 °C | 14.8 °C | REPAIR IMMEDIATELY |
|  | FP TX1 – OUTGOING F4 | OUTGOING FUSE CONNECTION/ RED PHASE | 106.2 °C | 61.2 °C | REPAIR IMMEDIATELY |
|  | FP TX1 – OUTGOING F6 | OUTGOING FUSE CONNECTION/ RED PHASE | 149.2 °C | 66.6 °C | REPAIR IMMEDIATELY |
|  | FP TX1 – OUTGOING F7 | OUTGOING FUSE CONNECTION/ RED PHASE | 219.2 °C | 167.6 °C | REPAIR IMMEDIATELY |

visual defect Summary

| NO. | EQUIPMENT | DEFECT DESCRIPTION | ELECTRICAL | NON-ELECTRICAL |
| --- | --- | --- | --- | --- |
| 1 | SUBSTATION | NO PADLOCK MAIN GATE |  | X |
| 2 | LIGHTING | MISSING | X |  |
| 3 | FIRE EXTINGUISHER | MISSING |  | X |

|  |  | Substation |  |  | SK KG MAJU JAYA |  |  |  |  |  |  |  |  |  |  |  |  | Date: 14/07/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | FP TX1 |  | Manufacturer |  |  |  |  |  |  |  |  | TOPRANK |  | Time: 07:40 PM |  |  |  |  |
|  |  | Model |  |  | J-SLOTTED |  | Rating |  |  |  |  |  |  |  |  | 1600A |  | Humidity: 63% |  |  |  |  |
|  |  | Area |  |  | OVERVIEW |  |  |  |  |  |  |  |  |  |  | Feeder No. |  | - |  |  |  |  |
| Feeder Name |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | - |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | - |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 652 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 37.1 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 32.0 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | - |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | - |  |  |  |  |
|  | Severity |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: Please refer the following page for details defect. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | SK KG MAJU JAYA |  |  |  |  |  |  |  |  |  |  |  |  | Date: 14/07/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | FP TX1 |  | Manufacturer |  |  |  |  |  |  |  |  | TOPRANK |  | Time: 07:40 PM |  |  |  |  |
|  |  | Model |  |  | J-SLOTTED |  | Rating |  |  |  |  |  |  |  |  | 1600A |  | Humidity: 63% |  |  |  |  |
|  |  | Area |  |  | LINK CONNECTION |  |  |  |  |  |  |  |  |  |  | Feeder No. |  | INCOMING F1 |  |  |  |  |
| Feeder Name |  | INCOMING F1 – RED PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 66.7 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 51.9 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 652 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 44.2 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 32.0 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 14.8 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Severity |  | REPAIR IMMEDIATELY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: Thermal image above indicates hot spot detected at INCOMING LINK CONNECTION. The anomaly is due to loosen or bad contact at the connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: To inspect, clean the contact surface and re-tighten the connection point. Replace defective parts if necessary. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | SK KG MAJU JAYA |  |  |  |  |  |  |  |  |  |  |  |  | Date: 14/07/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | FP TX1 |  | Manufacturer |  |  |  |  |  |  |  |  | TOPRANK |  | Time: 07:40 PM |  |  |  |  |
|  |  | Model |  |  | J-SLOTTED |  | Rating |  |  |  |  |  |  |  |  | 1600A |  | Humidity: 63% |  |  |  |  |
|  |  | Area |  |  | FUSE CONNECTION |  |  |  |  |  |  |  |  |  |  | Feeder No. |  | OUTGOING F4 |  |  |  |  |
| Feeder Name |  | OUTGOING F4 – RED PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 106.2 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 45.0 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 652 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 48.8 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 32.0 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 61.2 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Severity |  | REPAIR IMMEDIATELY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: Thermal image above indicates hot spot detected at OUTGOING FUSE CONNECTION. The anomaly is due to loosen or bad contact at the connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: To inspect, clean the contact surface and re-tighten the connection point. Replace defective parts if necessary. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | SK KG MAJU JAYA |  |  |  |  |  |  |  |  |  |  |  |  | Date: 14/07/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | FP TX1 |  | Manufacturer |  |  |  |  |  |  |  |  | TOPRANK |  | Time: 07:40 PM |  |  |  |  |
|  |  | Model |  |  | J-SLOTTED |  | Rating |  |  |  |  |  |  |  |  | 1600A |  | Humidity: 63% |  |  |  |  |
|  |  | Area |  |  | FUSE CONNECTION |  |  |  |  |  |  |  |  |  |  | Feeder No. |  | OUTGOING F6 |  |  |  |  |
| Feeder Name |  | OUTGOING F6 – RED PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 149.2 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | 82.6 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 652 |  |  |  |  |
|  | Average Temp. (Ar1) |  | 56.2 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 32.0 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | 66.6 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Severity |  | REPAIR IMMEDIATELY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: Thermal image above indicates hot spot detected at OUTGOING FUSE CONNECTION. The anomaly is due to loosen or bad contact at the connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: To inspect, clean the contact surface and re-tighten the connection point. Replace defective parts if necessary. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Substation |  |  | SK KG MAJU JAYA |  |  |  |  |  |  |  |  |  |  |  |  | Date: 14/07/2026 |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Equipment |  |  | FP TX1 |  | Manufacturer |  |  |  |  |  |  |  |  | TOPRANK |  | Time: 07:40 PM |  |  |  |  |
|  |  | Model |  |  | J-SLOTTED |  | Rating |  |  |  |  |  |  |  |  | 1600A |  | Humidity: 63% |  |  |  |  |
|  |  | Area |  |  | FUSE CONNECTION |  |  |  |  |  |  |  |  |  |  | Feeder No. |  | OUTGOING F7 |  |  |  |  |
| Feeder Name |  | OUTGOING F7 – RED PHASE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | IR IMAGE |  |  |  |  |  |  |  |  |  |  | VISUAL IMAGE |  |  |  |  |  |  |  |  |  |  |
|  | PARAMETER |  | VALUE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Spot Temp.1 (Sp1) |  | 219.2 °C |  |  |  |  |  |  |  |  |  |  |  | PARAMETER |  |  | VALUE |  |  |  |  |
|  | Spot Temp. 2 (Sp2) |  | *51.6 °C |  |  |  |  |  |  |  |  |  |  |  | Serial No. |  |  | 652 |  |  |  |  |
|  | Average Temp. (Ar1) |  | *53.5 °C |  |  |  |  |  |  |  |  |  |  |  | Heater (A) |  |  | - |  |  |  |  |
|  | Ambient Temp. |  | 32.0 °C |  |  |  |  |  |  |  |  |  |  |  | CB Position |  |  | - |  |  |  |  |
|  | Delta T ( ∆ T) |  | *167.6 °C |  |  |  |  |  |  |  |  |  |  |  | Busbar Position |  |  | - |  |  |  |  |
|  | Load (A) |  | - |  |  |  |  |  |  |  |  |  |  |  | Cable Type |  |  | XLPE |  |  |  |  |
|  | Severity |  | REPAIR IMMEDIATELY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis & Recommendations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Analysis: Thermal image above indicates hot spot detected at OUTGOING FUSE CONNECTION. The anomaly is due to loosen or bad contact at the connection point. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommendation: To inspect, clean the contact surface and re-tighten the connection point. Replace defective parts if necessary. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

SUBSTATION CONDITION

| SUBSTATION OVERVIEW |  | SIGNBOARD |
| --- | --- | --- |
| SWITCHGEAR |  | SWITCHGEAR NAMEPLATE |
| TRANSFORMER 1 |  | TRANSFORMER 1 NAMEPLATE |

SUBSTATION CONDITION

| TRANSFORMER 2 |  | TRANSFORMER 2 NAMEPLATE |
| --- | --- | --- |
| N/A |  | N/A |
| FEEDER PILLAR TX1 |  | FEEDER PILLAR TX1 NAMEPLATE |
| FEEDER PILLAR TX2 |  | FEEDER PILLAR TX2 NAMEPLATE |
| N/A |  | N/A |

SUBSTATION CONDITION

| EFI |  | SF6 INDICATOR |
| --- | --- | --- |
| BATTERY |  | BATTERY NAMEPLATE |
| FIRE EXTINGUISHER |  | FIRE EXTINGUISHER NAMEPLATE |
| N/A |  | N/A |

SUBSTATION CONDITION

| SWITCHGEAR PANEL NAME |  | LAST PREVENTIVE MAINTENANCE |
| --- | --- | --- |

VISUAL DEFECT

| SUBSTATION |  | LIGHTING |
| --- | --- | --- |
| NO PADLOCK MAIN GATE |  | MISSING |
| FIRE EXTINGUISHER |  |  |
| MISSING |  |  |

NORMAL/DEFECT STICKER

| NORMAL STICKER |  | DEFECT STICKER |
| --- | --- | --- |