## PCE Testsheet
81
[22 empty] | CBM CONDITION |  | NORMAL
DISTRIBUTION SUBSTATION (PCE) CBA TEST SHEET
STATE / AREA: |  | JOHOR / JOHOR BAHRU | [6 empty] | DATE | [5 empty] | 14/07/26 | [6 empty] | FUNCTIONAL LOCATION:
PE NAME: |  | O/D KG MAJU JAYA NO.1 | [6 empty] | TIME IN / OUT | [5 empty] | 2050 |  | / | 2140 |  |  |  | JJBU/PCE/K00191
V.I REF. NO | [8 empty] | TEV BACK GROUND / HUMIDITY | [5 empty] | 6 | dB | / | 68 |  | % |  | BACKGROUND TEMP : 32.9°C
SWITCHGEAR
DETAIL | [8 empty] | TEMPERATURE | [6 empty] | ULTRASOUND |  |  | TEV |  |  | REMARK
NO. | FDR. NO | FEEDER NAME |  | STATUS (TRIP / CLOSE) | LOAD (A) | CABLE TYPE/SIZE | HEATER (A) | SERIAL NO (ONLY BREAKER & OLU) | COMP | Tmin (°C) | Tmax (°C) | ΔT | Avg (°C) | FILE | REMARKS | dB | FILE | TYPE CHAR. | dB | PULSE/ CYCLE | TYPE CHAR.
1 | 2854 | PDT KG.MAJU JAYA |  | CLOSE |  | XLPE |  |  | CABLE | 31.3 | 31.4 |  |  | 248 |  | 0 |  |  | 6
BREAKER
TOP PANEL
PT
2 | 2852 | PAT KG MAJU JAYA NO.2 |  | CLOSE |  | XLPE |  |  | CABLE | 31.5 | 31.6 |  |  | 249 |  | 0 |  |  | 6
BREAKER
TOP PANEL
PT
3 | 2853 | TX 1000KVA |  | CLOSE |  | XLPE |  |  | CABLE | 31.3 | 31.4 |  |  | 250 |  | 0 |  |  | 6
BREAKER
TOP PANEL
PT
4 | [8 empty] | CABLE
BREAKER
TOP PANEL
PT
OVERVIEW | [8 empty] | CABLE |  |  |  | 31.8 | 242
BREAKER
[9 empty] | TOP PANEL |  |  |  | 31.5 | 246
PT
LOCAL TRANSFORMER
DETAILS |  |  |  |  | THERMOGRAHY |  |  |  |  | ULTRASOUND |  | DETAILS |  |  |  | THERMOGRAHY | [5 empty] | ULTRASOUND
TX ID | SERIAL NO | CABLE TYPE/SIZE | REMARK | COMP. | Tmin(°C) | Tmax(°C) | ΔT | Avg (°C) | FILE | dB | TYPE CHAR. | TX ID | SERIAL NO | CABLE TYPE/SIZE | COMP. | Tmin(°C) | Tmax(°C) | ΔT | Avg (°C) | FILE | dB | FILE | TYPE CHAR. | REMARKS
TX1 |  | XLPE |  | HT CABLE | 32 | 32.2 |  |  | 254 | 0 |  | TX3 |  |  | HT CABLE
|  |  |  | HT BUSHING | 35.3 | 35.5 |  |  | 253 | 0 |  |  |  |  | HT BUSHING
|  | XLPE |  | LV CABLE | 33.5 | 33.8 |  |  | 256 | [5 empty] | LV CABLE
|  |  |  | LV BUSHING | 35.8 | 36.1 |  |  | 255 | [5 empty] | LV BUSHING
|  |  |  | BODY | 37.5 | 42.7 |  |  | 251 | [5 empty] | BODY
TX2 |  |  |  | HT CABLE | [7 empty] | TX4 |  |  | HT CABLE
|  |  |  | HT BUSHING | [10 empty] | HT BUSHING
|  |  |  | LV CABLE | [10 empty] | LV CABLE
|  |  |  | LV BUSHING | [10 empty] | LV BUSHING
|  |  |  | BODY | [10 empty] | BODY
LV DISTRIBUTION BOARD/FEEDER PILLAR/OTHERS
1 | LVDB / FP 1 |  | INC. 1 | INC. 2 |  | INC. 3 |  | F1 | F2 | F3 | F4 | F5 | F6 | F7 | F8 | F9 | F10
| CABLE TYPE / SIZE |  | XLPE |  |  |  |  | F1: XLPE; F2: XLPE; F3: XLPE
2 | LVDB / FP 2 |  | INC. 1 | INC. 2 |  | INC. 3 |  | F1 | F2 | F3 | F4 | F5 | F6 | F7 | F8 | F9 | F10
CABLE TYPE / SIZE
NO | LVDB / FP | DEFECTIVE FEEDER NAME |  | Tmin(°C) | Tmax(°C) | ΔT | FILE | XLPE F1: Avg (°C); XLPE F2: REMARK; XLPE F10: FP |  | TX1 |  | J-SLOTTED
| INC 1 | [6 empty] | XLPE F10: Manufacturer : |  |  |  | N/A
| INC 2 | [6 empty] | XLPE F10: Serial No. : |  |  |  | N//A
| F1 | [6 empty] | XLPE F10: Rating : |  |  |  | 800A
| F2 | [6 empty] | XLPE F10: LVDB |  | TX2
| F3 | [6 empty] | XLPE F10: Manufacturer :
| F4 | [6 empty] | XLPE F10: Serial No. :
| F5 | [6 empty] | XLPE F10: Rating :
F6
F7
F8
Battery Bank
Black Box 1
Black Box 2
Lightning Arrester
Dropout Fuse
Auto Recloser
LBS
| Tested by (Name & Signature) : | [6 empty] | XLPE F8: TNB Supervisor/Engineer (Name & Signature) :
Ver. : 1-2019
Note on P5: ====== ID#AAAB__nLh4Q tc={82553E5C-51BD-4126-8C45-02F3CBDD3B0E} (2026-07-14 09:59:25) [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 24hrs format e.g. 2100
Note on B49: ====== ID#AAAB__nLh3s Author (2026-07-14 09:59:25) Tambahan
Note on B50: ====== ID#AAAB__nLh34 Author (2026-07-14 09:59:25) Tambahan
Note on B51: ====== ID#AAAB__nLh3o Author (2026-07-14 09:59:25) Tambahan
Note on B52: ====== ID#AAAB__nLh30 Author (2026-07-14 09:59:25) Tambahan
Note on B53: ====== ID#AAAB__nLh38 Author (2026-07-14 09:59:25) Tambahan
Note on B54: ====== ID#AAAB__nLh4I Author (2026-07-14 09:59:25) Tambahan
Note on B55: ====== ID#AAAB__nLh3w Author (2026-07-14 09:59:25) Tambahan
Note on B58: ====== ID#AAAB__nLh4M Author (2026-07-14 09:59:25) Tambahan
Note on B62: ====== ID#AAAB__nLh4E Author (2026-07-14 09:59:25) Tambahan
Note on B63: ====== ID#AAAB__nLh4A Author (2026-07-14 09:59:25) Tambahan
Note on B65: ====== ID#AAAB__nLh4U Author (2026-07-14 09:59:25) Tambahan

## PCE VI
Vi no mat, | [10 empty] | TYPE | PCE
VISUAL INSPECTION CHECKLIST FOR 11kV SUBSTATION
DATE:
P/E Name (ERMS): | [7 empty] | F/L NO (ERMS):
P/E Name (SITE): | PE O/DOOR KG MAJU JAYA # 1 | [6 empty] | F/L NO (SITE): | JJBU/PCE/K00191
GPS Coordinate: | 1.583366, 103.718120
PCE Type: | INDOOR |  |  | OUTDOOR | ✅ | COMPACT |  | ATTACH BUILDING |  | PAT |  | OTHER
PCE Area | NORMAL | ✅ |  | INDUSTRIAL |  | COASTAL
Switcgear Type 1: | RMU OIL |  |  | RMU SF6 | ✅ | MRMU |  | VCB |  | OCB |  | OTHER
Manufacturer/Model: | INDKOM |  |  | INS24
Switchgear Manufactured Date: | 2015-03-08 |  |  |  |  | Switchgear Rating : |  | 12kV |  |  | RMU SF6 / OIL S/N : |  | 15072115279DE
Switcgear Type 2: | RMU OIL |  |  | RMU SF6 |  | MRMU |  | VCB |  | OCB
Manufacturer/Modal:
Switchgear Manufactured Date: | [5 empty] | Switchgear Rating : |  |  |  |  | RMU SF6 / OIL S/N :
No. of Transformer: | 1
Tx 1: | Type | H/S | KVA | 1000kVA | Construction Yr: |  | 2015 | Manufacturer: | SGB |  |  | S/N : | 727812
Tx 2: | Type |  | KVA |  | Construction Yr: |  |  | Manufacturer: |  |  |  | S/N :
Tx 3: | Type |  | KVA |  | Construction Yr: |  |  | Manufacturer: |  |  |  | S/N :
Tx 4: | Type |  | KVA |  | Construction Yr: |  |  | Manufacturer: |  |  |  | S/N :
KEJANGGALAN
1. Signboard: |  | Good | ✅ | Not Good |  | Remarks
2. Earth connection: |  | Good | ✅ | Not Good |  | Remarks
3. EFI Functioning: |  | Good | ✅ | Not Good |  | Remarks
4. Heater Functioning: |  | Good |  | Not Good |  | Remarks
5. Labelling @Switchgear: |  | Good | ✅ | Not Good |  | Remarks
6. Labelling @ LVDB: |  | Good | ✅ | Not Good |  | Remarks
7. Gas Pressure: |  | Good | ✅ | Not Good |  | Remarks
8. Tx Guard: |  | YES | ✅ | NO |  | Remarks
9. Tx Oil Level (conservator tank): |  | Good |  | Not Good |  | Remarks
10. Tx Oil Leak: |  | YES |  | NO | ✅ | Remarks
11. Tx Bushing: |  | Good | ✅ | Not Good |  | Remarks
12. Top Demand Indicator (@LVDB): |  | Good | ✅ | Not Good |  | Remarks
13. Link/fuse Holder: |  | Good | ✅ | Not Good |  | Remarks
14. LV Termination: |  | Good | ✅ | Not Good |  | Remarks
15. Rubber Mat: |  | YES |  | NO | ✅ | Remarks
16. Trenching: |  | Good | ✅ | Not Good |  | Remarks
17. Battery Voltage: |  | Good |  | Not Good |  | Remarks
18. Lighting: |  | Good | ✅ | Not Good |  | Remarks
19. Roof Condition: |  | Good | ✅ | Not Good |  | Remarks
20. Fire Fighting |  | Valid | ✅ | Expired |  | Remarks | Expiry Date: 11/9/26 |  |  | No. of missing portable : |  | -
21. Fence/door condition: |  | Good | ✅ | Not Good |  | Remarks
22. Cleanliness/Bushes: |  | YES |  | NO | ✅ | Remarks
23. Vandalisme |  | YES |  | NO | ✅ | Remarks
24. Other Findings:
Tested by (Name & Signature) : | [5 empty] | TNB Supervisor / Engineer (Name & Signature) :
Date : | [5 empty] | Date :
Ver. : 1-2019

## RAW DATA
| START | END
IR | 242 | 259
DG | 3933 | 3947

## vi_library (hidden)
SUBSTATION_TYPE | CHECKMARK
INDOOR | ✅
OUTDOOR
PAT
COMPACT
ATTACHED BUILDING
INDOOR/COMPACT
OUTDOOR/COMPACT

## substation_library (hidden)
AREA | STATE
JOHOR BAHRU | JOHOR

## equipment_library (hidden)
SWITCHGEAR_TYPE | CB_POSITION_RMU | CB_POSITION_VCB | BUSBAR_POSITION | CABLE_TYPE | SWG_MANUFACTURER | SWG_MODEL | SWG_RATING | TX_MANUFACTURER | TX_MODEL | TX_RATING | TX_AREA | LV_MANUFACTURER | LV_MODEL | LV_RATING | BATT_MANUFACTURER | BATT_MODEL
RMU SF6 | CLOSE | SERVICE/CLOSE | MAIN | XLPE |  |  | 6.6kV |  | H/S | 100kVA | OVERVIEW |  | DIN TYPE | 1600A | BERKAT INSAF | SEB100-30-10
MRMU SF6 | TRIP | SERVICE/TRIP | RESERVE | PILC |  |  | 12kV |  | C/T | 300kVA | OVERVIEW TOP |  | J-SLOTTED | 1000A | SUNPOWER
RMU OIL |  | TEST/TRIP | MAIN/RESERVE | N/A |  |  | 24kV |  |  | 500kVA | HV BUSHING |  |  | 800A
VCB |  | RACK OUT | N/A | NOT ACCESSIBLE |  |  | 36kV |  |  | 750kVA | HV CABLE |  |  | 400A
GIS | [9 empty] | 1000kVA | HV CABLE SPLIT |  |  | N/A
ACB | [9 empty] | N/A | LV BUSHING
PAT | [9 empty] | NOT ACCESSIBLE | LV CABLE